## Cable
Room Nr | Connected to DF | Length m | Width m | Size sqm | Nr Dou_Outlets | Dist_To_DF | AVG_In Room | Cable for room | Room Type
1.1 | MDF | 6.5 | 8.5 | 55.25 | 6 | 9.4 | 14 | 352.8 | A
1.2 | MDF | 8.5 | 6.5 | 55.25 | 6 | 16.11 | 5 | 325.32 | B
1.3 | MDF
1.4 | MDF | 5.5 | 8.5 | 46.75 | 5 | 21.82 | 11 | 388.2 | C
1.5 | MDF | 5.5 | 8.5 | 46.75 | 5 | 27.82 | 11 | 448.2 | C
1.6 | MDF | 5.5 | 8.5 | 46.75 | 5 | 33.53 | 11 | 505.3 | C
1.7 | MDF | 5.5 | 8.5 | 46.75 | 5 | 39.53 | 11 | 565.3 | C
1.8 | MDF | 5.5 | 8.5 | 46.75 | 5 | 45.24 | 11 | 622.4 | C
1.9 | BATHROOM
1.10
1.11 | MDF | 8.5 | 11.5 | 97.75 | 10 | 0.5 | 11 | 350 | D
1.12 | MDF | 20 | 16.5 | 330 | 33 | 5 | 22 | 2178 | F
1.13 | MDF | 6.5 | 11.5 | 74.75 | 8 | 84.64 | 17 | 1722.24 | E
1.14 | MDF | 6.5 | 11.5 | 74.75 | 8 | 91.78 | 17 | 1836.48 | E
1.15 | MDF | 6.5 | 11.5 | 74.75 | 8 | 98.78 | 17 | 1948.48 | E
1.16 | MDF | 6.5 | 11.5 | 74.75 | 8 | 105.92 | 17 | 2062.72 | E
1.17 | MDF | 6.5 | 11.5 | 74.75 | 8 | 112.92 | 17 | 2174.72 | E
1.22 | MDF | 10 | 20 | 200 | 20 | 17.5 | 14 | 1500 | G
Subtotal MDF |  |  |  |  | 140 |  |  | 16980.16
1.18 | IDF1 | 6.5 | 11.5 | 74.75 | 8 | 32 | 17 | 880 | E
1.19 | IDF1 | 6.5 | 11.5 | 74.75 | 8 | 27 | 17 | 800 | E
1.20 | BATHROOM
1.21
1.23 | IDF1 | 10 | 20 | 200 | 20 | 0.5 | 14 | 820 | G
1.24 | IDF1 | 9 | 10 | 90 | 9 | 45 | 20 | 1278 | H
1.25 | IDF1 | 9 | 10 | 90 | 9 | 40 | 20 | 1188 | H
1.26 | IDF1 | 6.5 | 9 | 58.5 | 6 | 12.54 | 18 | 438.48 | I
1.27 | IDF1 | 6.5 | 9 | 58.5 | 6 | 21.88 | 18 | 550.56 | I
1.28 | IDF1
1.29 | IDF1 | 4.5 | 9.5 | 42.75 | 5 | 11.5 | 13 | 305 | J
1.30 | IDF1 | 4.5 | 9.5 | 42.75 | 5 | 17 | 13 | 360 | J
1.31 | IDF1 | 4.5 | 9.5 | 42.75 | 5 | 22.5 | 13 | 415 | J
1.32 | IDF1 | 4.5 | 9.5 | 42.75 | 5 | 28 | 13 | 470 | J
1.33 | IDF1 | 4.5 | 9.5 | 42.75 | 5 | 33.5 | 13 | 525 | J
1.34 | BATHROOM
1.35
1.36 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 10.5 | 18 | 483 | K
1.37 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 17.5 | 18 | 581 | K
1.38 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 23.5 | 18 | 665 | K
1.39 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 29.5 | 18 | 749 | K
1.40 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 35.5 | 18 | 833 | K
1.41 | IDF1 | 5.5 | 12.5 | 68.75 | 7 | 41.5 | 18 | 917 | K
Subtotal IDF1 |  |  |  |  | 133 |  |  | 12258.04
2.1 | IDF2 | 6.5 | 8.5 | 55.25 | 6 | 9.4 | 14 | 352.8 | A
2.2 | IDF2 | 8.5 | 6.5 | 55.25 | 6 | 16.11 | 5 | 325.32 | B
2.3 | IDF2
2.4 | IDF2 | 5.5 | 8.5 | 46.75 | 5 | 21.82 | 11 | 388.2 | C
2.5 | IDF2 | 5.5 | 8.5 | 46.75 | 5 | 27.82 | 11 | 448.2 | C
2.6 | IDF2 | 5.5 | 8.5 | 46.75 | 5 | 33.53 | 11 | 505.3 | C
2.7 | IDF2 | 5.5 | 8.5 | 46.75 | 5 | 39.53 | 11 | 565.3 | C
2.8 | IDF2 | 5.5 | 8.5 | 46.75 | 5 | 45.24 | 11 | 622.4 | C
2.9 | BATHROOM
2.10
2.11 | IDF2 | 8.5 | 11.5 | 97.75 | 10 | 0.5 | 11 | 350 | D
2.12 | IDF2 | 20 | 16.5 | 330 | 33 | 5 | 22 | 2178 | F
2.13 | IDF2 | 6.5 | 11.5 | 74.75 | 8 | 84.64 | 17 | 1722.24 | E
2.14 | IDF2 | 6.5 | 11.5 | 74.75 | 8 | 91.78 | 17 | 1836.48 | E
2.15 | IDF2 | 6.5 | 11.5 | 74.75 | 8 | 98.78 | 17 | 1948.48 | E
2.16 | IDF2 | 6.5 | 11.5 | 74.75 | 8 | 105.92 | 17 | 2062.72 | E
2.17 | IDF2 | 6.5 | 11.5 | 74.75 | 8 | 112.92 | 17 | 2174.72 | E
2.22 | IDF2 | 10 | 20 | 200 | 20 | 17.5 | 14 | 1500 | G
Subtotal IDF2 |  |  |  |  | 140 |  |  | 16980.16
2.18 | IDF3 | 6.5 | 11.5 | 74.75 | 8 | 32 | 17 | 880 | E
2.19 | IDF3 | 6.5 | 11.5 | 74.75 | 8 | 27 | 17 | 800 | E
2.20 | BATHROOM
2.21
2.23 | IDF3 | 10 | 20 | 200 | 20 | 0.5 | 14 | 820 | G
2.24/25 | IDF3 | 5 | 14 | 70 | 7 | 56.07 | 17 | 1106.98 | L
2.26 | IDF3 | 9 | 6.5 | 58.5 | 6 | 12.54 | 18 | 438.48 | I
2.27 | IDF3 | 6.5 | 9 | 58.5 | 6 | 21.88 | 18 | 550.56 | I
2.28 | IDF3
2.29 | IDF3 | 4.5 | 9.5 | 42.75 | 5 | 11.5 | 13 | 305 | J
2.30 | IDF3 | 4.5 | 9.5 | 42.75 | 5 | 17 | 13 | 360 | J
2.31 | IDF3 | 4.5 | 9.5 | 42.75 | 5 | 22.5 | 13 | 415 | J
2.32 | IDF3 | 4.5 | 9.5 | 42.75 | 5 | 28 | 13 | 470 | J
2.33 | IDF3 | 4.5 | 9.5 | 42.75 | 5 | 33.5 | 13 | 525 | J
2.34 | BATHROOM
2.35
2.36 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 10.5 | 18 | 483 | K
2.37 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 17.5 | 18 | 581 | K
2.38 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 23.5 | 18 | 665 | K
2.39 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 29.5 | 18 | 749 | K
2.40 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 35.5 | 18 | 833 | K
2.41 | IDF3 | 5.5 | 12.5 | 68.75 | 7 | 41.5 | 18 | 917 | K
Subtotal IDF3 |  |  |  |  | 122 |  |  | 10899.02
Total_Build |  |  |  |  | 535 |  |  | 57117.38
[7 empty] | 305M Boxes | 207
[7 empty] | 2km Rols | 29
To check AVG linkspan |  | 53.3807
Adapt technical reserve amount of cable according to design, example is for 3m, could be more
Do not change
From your design
From detailed calcullus of prototype room/rooms
Note on H1: ====== ID#AAAB25SOS0w Emil Cebuc (2026-04-01 14:28:17) From detaild design
Note on I1: ====== ID#AAAB25SOS00 Emil Cebuc (2026-04-01 14:28:17) 3m for in rack cabling

## Fiber
Fiber optic cable length
Cable Source | Target | Length (m)
A0 | B0 | 35
B1 | A1 | 85
C0 | D0 | 35
D1 | C1 | 85
A1 | C1 | 5
D0 | B0 | 5
A0 | C0 | 5
D1 | B1 | 5
Total fiber optic cable length |  | 260

## Tech Stack
Device | Estimated Average Traffic [Mpbs]
Workstation | 25
IP phone | 0.1
Access Point | 300
Concurrency factor | 0.7
Floor | Room Type |  | Number of rooms | Total Estimated Traffic [Gbps] | Estimated Traffic/Room [Gbps] | Number of workstations | Number of IP phones | Number of access points | Number of simple outlets
GROUND FLOOR | A |  | 1 | 0.38507 | 385.07 | 10 | 1 | 1 | 12
| B |  | 1 | 0.38507 | 385.07 | 10 | 1 | 1 | 12
| C |  | 5 | 1.7503 | 350.07 | 8 | 1 | 1 | 50
| D |  | 1 | 0.70014 | 700.14 | 16 | 2 | 2 | 20
| E |  | 7 | 3.1855 | 455.07 | 14 | 1 | 1 | 112
| F |  | 1 | 1.5226 | 1522.57 | 63 | 1 | 2 | 66
| G |  | 2 | 2.1351 | 1067.57 | 37 | 1 | 2 | 80
| H |  | 2 | 1.3651 | 682.57 | 15 | 1 | 2 | 36
| I |  | 2 | 0.77014 | 385.07 | 10 | 1 | 1 | 24
| J |  | 5 | 1.7503 | 350.07 | 8 | 1 | 1 | 50
| K |  | 6 | 2.5204 | 420.07 | 12 | 1 | 1 | 84
| L |  | 0 | 0 | 420.07 | 12 | 1 | 1 | 0
FIRST FLOOR | A |  | 1 | 0.38507 | 385.07 | 10 | 1 | 1 | 12
| B |  | 1 | 0.38507 | 385.07 | 10 | 1 | 1 | 12
| C |  | 5 | 1.7503 | 350.07 | 8 | 1 | 1 | 50
| D |  | 1 | 0.70014 | 700.14 | 16 | 2 | 2 | 20
| E |  | 7 | 3.1855 | 455.07 | 14 | 1 | 1 | 112
| F |  | 1 | 1.5226 | 1522.57 | 63 | 1 | 2 | 66
| G |  | 2 | 2.1351 | 1067.57 | 37 | 1 | 2 | 80
| H |  | 0 | 0 | 682.57 | 15 | 1 | 2 | 0
| I |  | 2 | 0.77014 | 385.07 | 10 | 1 | 1 | 24
| J |  | 5 | 1.7503 | 350.07 | 8 | 1 | 1 | 50
| K |  | 6 | 2.5204 | 420.07 | 12 | 1 | 1 | 84
| L |  | 1 | 0.42007 | 420.07 | 12 | 1 | 1 | 14
| Estimated peak traffic value in network [Gbps] |  |  | 32 |  |  | Total number of simple outlets |  | 1070
[7 empty] | Total number of IP Phones |  | 67
[7 empty] | Total number of AP |  | 75
[7 empty] | Total number of WS |  | 928
DF | Number of WS |  | Number of AP | Number of IP Phones | Number of Room Types Covered
[5 empty] | A | B | C | D | E | F | G | H | I | J | K | L
MDF | 246 |  | 18 | 16 | 1 | 1 | 5 | 1 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0
IDF1 | 227 |  | 21 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 2 | 5 | 6 | 0
IDF2 | 246 |  | 18 | 16 | 1 | 1 | 5 | 1 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0
IDF3 | 209 |  | 18 | 17 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 5 | 6 | 1
Total outlets | 1070
Equipment
Type | Choice 1 (CISCO) |  |  |  | Number of Room Types Covered A: Choice 2; Number of Room Types Covered E: DF
| Name | Required number/DF | Price | Link | Number of Room Types Covered A: Name; Number of Room Types Covered B: Required number/DF; Number of Room Types Covered C: Price; Number of Room Types Covered D: Link
Wireless Mangement | CW9800L | 1 | 3686.6 | link | Number of Room Types Covered A: HPE Aruba Networking Central; Number of Room Types Covered B: 1; Number of Room Types Covered C: subscription; Number of Room Types Covered D: link
CHASSIS | Cisco Catalyst 9410R | 1 | 6100.82 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6410 v2 Switch; Number of Room Types Covered B: 1; Number of Room Types Covered C: 26334.7; Number of Room Types Covered D: link; Number of Room Types Covered E: MDF
SUPERVISOR | C9400-SUP-1XL | 1 | 7123.14 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 Management Module; Number of Room Types Covered B: 1; Number of Room Types Covered C: 14125.61; Number of Room Types Covered D: link
LINE CARD (WS) | C9400-LC-48P | 6 | 4959.83 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X39C; Number of Room Types Covered B: 6; Number of Room Types Covered C: 5350; Number of Room Types Covered D: link
LINE CARD (IPPHONE)
OF CONNECTOR | QSFP+ | 14 | 343.64 | link | Number of Room Types Covered A: HP JL310A; Number of Room Types Covered B: 12; Number of Room Types Covered C: 1295; Number of Room Types Covered D: link
LINE CARD (OF) | C9400-LC-12QC (12x40GE) | 1 | 17336.86 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X45C; Number of Room Types Covered B: 1; Number of Room Types Covered C: 47650; Number of Room Types Covered D: link
LINE CARD (AP) | C9400-LC-48UX | 1 | 5015.78 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 24p S1T83A; Number of Room Types Covered B: 1; Number of Room Types Covered C: 15545; Number of Room Types Covered D: link
ACCESS POINT | Cisco Wireless 9178 | 18 | 5455.89 | link | Number of Room Types Covered A: HPE Aruba Networking AP‑765; Number of Room Types Covered B: 18; Number of Room Types Covered C: 1475.37; Number of Room Types Covered D: link
FIREWALL | Cisco Secure Firewall 4245 | 1 | 152,257.81 | link | Number of Room Types Covered A: PALO-ALTO PA-3440; Number of Room Types Covered B: 1; Number of Room Types Covered C: 68179.32; Number of Room Types Covered D: link
IP PHONES | Cisco IP Phone 8861 | 16 | 366.2 | link | Number of Room Types Covered A: HP 82M93AA; Number of Room Types Covered B: 16; Number of Room Types Covered C: 194.99; Number of Room Types Covered D: link
CHASSIS | Cisco Catalyst 9410R | 1 | 6100.82 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6410 v2 Switch; Number of Room Types Covered B: 1; Number of Room Types Covered C: 26334.7; Number of Room Types Covered D: link; Number of Room Types Covered E: IDF1
SUPERVISOR | C9400-SUP-1XL | 1 | 7123.14 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 Management Module; Number of Room Types Covered B: 1; Number of Room Types Covered C: 14125.61; Number of Room Types Covered D: link
LINE CARD (WS) | C9400-LC-48P | 6 | 4959.83 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X39C; Number of Room Types Covered B: 6; Number of Room Types Covered C: 5350; Number of Room Types Covered D: link
LINE CARD (IPPHONE)
LINE CARD (OF) | C9400-LC-12QC | 1 | 17336.86 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X45C; Number of Room Types Covered B: 1; Number of Room Types Covered C: 47650; Number of Room Types Covered D: link
OF CONNECTOR | QSFP+ | 12 | 343.64 | link | Number of Room Types Covered A: HP JL310A; Number of Room Types Covered B: 12; Number of Room Types Covered C: 1295; Number of Room Types Covered D: link
LINE CARD (AP) | C9400-LC-48UX | 1 | 5015.78 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 24p S1T83A; Number of Room Types Covered B: 1; Number of Room Types Covered C: 15545; Number of Room Types Covered D: link
ACCESS POINT | Cisco Wireless 9179F | 21 | 5455.89 | link | Number of Room Types Covered A: HPE Aruba Networking AP‑765; Number of Room Types Covered B: 21; Number of Room Types Covered C: 1475.37; Number of Room Types Covered D: link
IP PHONES | Cisco IP Phone 8861 | 18 | 366.2 | link | Number of Room Types Covered A: HP 82M93AA; Number of Room Types Covered B: 18; Number of Room Types Covered C: 194.99; Number of Room Types Covered D: link
CHASSIS | Cisco Catalyst 9410R | 1 | 6100.82 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6410 v2 Switch; Number of Room Types Covered B: 1; Number of Room Types Covered C: 26334.7; Number of Room Types Covered D: link; Number of Room Types Covered E: IDF2
SUPERVISOR | C9400-SUP-1XL | 1 | 7123.14 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 Management Module; Number of Room Types Covered B: 1; Number of Room Types Covered C: 14125.61; Number of Room Types Covered D: link
LINE CARD (WS) | C9400-LC-48P | 6 | 4959.83 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X39C; Number of Room Types Covered B: 6; Number of Room Types Covered C: 5350; Number of Room Types Covered D: link
LINE CARD (IPPHONE)
LINE CARD (OF) | C9400-LC-12QC | 1 | 17336.86 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X45C; Number of Room Types Covered B: 1; Number of Room Types Covered C: 47650; Number of Room Types Covered D: link
OF CONNECTOR | QSFP+ | 12 | 343.64 | link | Number of Room Types Covered A: HP JL310A; Number of Room Types Covered B: 12; Number of Room Types Covered C: 1295; Number of Room Types Covered D: link
LINE CARD (AP) | C9400-LC-48UX | 1 | 5015.78 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 24p S1T83A; Number of Room Types Covered B: 1; Number of Room Types Covered C: 15545; Number of Room Types Covered D: link
ACCESS POINT | Cisco Wireless 9179F | 18 | 5455.89 | link | Number of Room Types Covered A: HPE Aruba Networking AP‑765; Number of Room Types Covered B: 18; Number of Room Types Covered C: 1475.37; Number of Room Types Covered D: link
IP PHONES | Cisco IP Phone 8861 | 16 | 366.2 | link | Number of Room Types Covered A: HP 82M93AA; Number of Room Types Covered B: 16; Number of Room Types Covered C: 194.99; Number of Room Types Covered D: link
CHASSIS | Cisco Catalyst 9410R | 1 | 6100.82 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6410 v2 Switch; Number of Room Types Covered B: 1; Number of Room Types Covered C: 26334.7; Number of Room Types Covered D: link; Number of Room Types Covered E: IDF3
SUPERVISOR | C9400-SUP-1XL | 1 | 7123.14 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 Management Module; Number of Room Types Covered B: 1; Number of Room Types Covered C: 14125.61; Number of Room Types Covered D: link
LINE CARD (WS) | C9400-LC-48P | 5 | 4959.83 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X39C; Number of Room Types Covered B: 5; Number of Room Types Covered C: 5350; Number of Room Types Covered D: link
LINE CARD (IPPHONE)
LINE CARD (OF) | C9400-LC-12QC | 1 | 17336.86 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 R0X45C; Number of Room Types Covered B: 1; Number of Room Types Covered C: 47650; Number of Room Types Covered D: link
OF CONNECTOR | QSFP+ | 12 | 343.64 | link | Number of Room Types Covered A: HP JL310A; Number of Room Types Covered B: 12; Number of Room Types Covered C: 1295; Number of Room Types Covered D: link
LINE CARD (AP) | C9400-LC-48UX | 1 | 5015.78 | link | Number of Room Types Covered A: HPE Aruba Networking CX 6400 24p S1T83A; Number of Room Types Covered B: 1; Number of Room Types Covered C: 15545; Number of Room Types Covered D: link
ACCESS POINT | Cisco Wireless 9179F | 18 | 5455.89 | link | Number of Room Types Covered A: HPE Aruba Networking AP‑765; Number of Room Types Covered B: 18; Number of Room Types Covered C: 1475.37; Number of Room Types Covered D: link
IP PHONES | Cisco IP Phone 8861 | 17 | 366.2 | link | Number of Room Types Covered A: HP 82M93AA; Number of Room Types Covered B: 17; Number of Room Types Covered C: 194.99; Number of Room Types Covered D: link
|  |  | 710978.24 |  | Number of Room Types Covered C: 791727.64
Public Ip | Private Ip
203.0.113.0 | 10.1.0.0
VLAN Name | Network ID | Gateway | Last Usable IP | Broadcast | Number of Room Types Covered A: Mask; Number of Room Types Covered B: Target Use; Number of Room Types Covered C: Max Capacity
Management | 10.1.10.0 | 10.1.10.1 | 10.1.10.254 | 10.1.10.255 | Number of Room Types Covered A: /24; Number of Room Types Covered B: 254; Number of Room Types Covered C: 254
IP_Phone_Data | 10.1.19.0 | 10.1.19.1 | 10.1.19.254 | 10.1.19.255 | Number of Room Types Covered A: /24; Number of Room Types Covered B: 254; Number of Room Types Covered C: 254
IP_Phone | 10.1.20.0 | 10.1.20.1 | 10.1.20.254 | 10.1.20.255 | Number of Room Types Covered A: /24; Number of Room Types Covered B: 254; Number of Room Types Covered C: 254
Wireless | 10.1.32.0 | 10.1.32.1 | 10.1.35.254 | 10.1.35.255 | Number of Room Types Covered A: /22; Number of Room Types Covered B: 1000; Number of Room Types Covered C: 1022
Data_Staff | 10.1.40.0 | 10.1.40.1 | 10.1.40.254 | 10.1.40.255 | Number of Room Types Covered A: /24; Number of Room Types Covered B: 254; Number of Room Types Covered C: 254
Data_Guest | 10.1.50.0 | 10.1.50.1 | 10.1.50.254 | 10.1.50.255 | Number of Room Types Covered A: /24; Number of Room Types Covered B: 254; Number of Room Types Covered C: 254
HR | 10.1.100.0 | 10.1.100.1 | 10.1.100.62 | 10.1.100.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Finance | 10.1.110.0 | 10.1.110.1 | 10.1.110.62 | 10.1.110.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
IT_Ops | 10.1.120.0 | 10.1.120.1 | 10.1.120.62 | 10.1.120.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Legal | 10.1.130.0 | 10.1.130.1 | 10.1.130.62 | 10.1.130.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Sales_North | 10.1.140.0 | 10.1.140.1 | 10.1.140.62 | 10.1.140.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Sales_South | 10.1.150.0 | 10.1.150.1 | 10.1.150.62 | 10.1.150.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Sales_East | 10.1.160.0 | 10.1.160.1 | 10.1.160.62 | 10.1.160.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Sales_West | 10.1.170.0 | 10.1.170.1 | 10.1.170.62 | 10.1.170.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Mktg_Digital | 10.1.180.0 | 10.1.180.1 | 10.1.180.62 | 10.1.180.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Mktg_Brand | 10.1.190.0 | 10.1.190.1 | 10.1.190.62 | 10.1.190.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Frontend_Dev | 10.1.200.0 | 10.1.200.1 | 10.1.200.62 | 10.1.200.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Backend_Dev | 10.1.210.0 | 10.1.210.1 | 10.1.210.62 | 10.1.210.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
QA_Test | 10.1.220.0 | 10.1.220.1 | 10.1.220.62 | 10.1.220.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Logistics | 10.1.230.0 | 10.1.230.1 | 10.1.230.62 | 10.1.230.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Purchasing | 10.1.240.0 | 10.1.240.1 | 10.1.240.62 | 10.1.240.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Exec_Suite | 10.1.250.0 | 10.1.250.1 | 10.1.250.62 | 10.1.250.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
DevOps_Primary | 10.2.0.0 | 10.2.0.1 | 10.2.0.62 | 10.2.0.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
DevOps_Second | 10.2.10.0 | 10.2.10.1 | 10.2.10.62 | 10.2.10.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
SRE_Internal | 10.2.20.0 | 10.2.20.1 | 10.2.20.62 | 10.2.20.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Security_Ops | 10.2.30.0 | 10.2.30.1 | 10.2.30.62 | 10.2.30.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
Training_Lab | 10.2.40.0 | 10.2.40.1 | 10.2.40.62 | 10.2.40.63 | Number of Room Types Covered A: /26; Number of Room Types Covered B: 48; Number of Room Types Covered C: 62
[6 empty] | Total target Use | Max IP capacity
[6 empty] | 3134 | 3408

## MDF
Open Frame Server 44U Rack
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica W | Caldura disipata BTU/h | ORG Vert
Organizator de cabluri vertical | 1 | OF Patch Panel | PP-72X100G-SMF | 72 |  |  | Organizator de cabluri vertical
| 13 | Chassis | Cisco Catalyst 9410R
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | OF Line Card | C9400-LC-12QC (12x40GE) | 12 | 280 | 954.8
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (IP Phone) | C9400-LC-48P | 48 | 845 | 250
|  | Line Card (AP) | C9400-LC-48UX | 48 | 1630 | 250 |  | Power required in chassis | 4380
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950 |  | Power provided by chassis | 9600
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Catalyst 9410R Fan Tray | C9410-FAN |  | 600 | 2046
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | EMPTY SPACE FOR VENTILATION
| 1 | Firewall | Cisco Secure Firewall 4245 |  | 1380 | 3000
|  | Firewall 4245 Fan Module | FPR4200-FAN |  | 45 | 153.45
|  | Firewall 4245 Fan Module | FPR4200-FAN |  | 45 | 153.45
|  | Firewall 4245 Fan Module | FPR4200-FAN |  | 45 | 153.45
| 2 | EMPTY SPACE FOR VENTILATION
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
Total | 44 |  |  |  |  | 18206.4
|  |  |  | Required UPS power [W] | 11115
|  |  |  | Available UPS power [W] | 20000
|  |  | Consum electric AC | Racire AC
| AC 1 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
| AC 2 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
|  | Total | 11400 | 38000
| Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 280
| Nr prize disponibil in PP UTP in acest rack | 336
Note
Se lasa loc liber in Rack cca 10-20% din spatiu pentru dezvoltari ulterioare
Daca nu incape intrun singur Rack se pot pune mai multe in fieacre DF, UPS /uri se pun in fiecare Rack
Rack sunt de maxim 48 U sau 52 U inaltime
Puterea disponibila in UPS sa fie cu 30% mai mare decat total putere necesar
Daca sunt mai multe UPS-uri se distribuie sarcina intre ele
Capacitatea bateriilor/acumultorilor din UPS se determina in asa fel incat sa asigure o functionare de 30 la 60 minute la sarcina medie
Total porturi UTP din Switchuri intre 70 si 100 % din nr de prize simple care se conecteaza la un DF, functie de strategia aleasa
nr de porturi total din Patch Pannel UTP trebuie sa fie mai mare sau egal cu nr de prize simple care se conecteaza la un DF
Echipamentele de racire se pun in fiecare DF si vor trebuii sa aibe capacitatea de racire cu cca 30% mai mare decat total Caldura dispata
Echipamentele de racire, Aer Conditionat de uz industrial nu sunt alimentate din UPS
Foia de calcul se replica pentru fiecare DF in parte
Note on C39: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure
Note on C40: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure

## IDF1
Open Frame Server 44U Rack
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica W | Caldura disipata BTU/h | ORG Vert
Organizator de cabluri vertical | 1 | OF Patch Panel | PP-72X100G-SMF | 72 |  |  | Organizator de cabluri vertical
| 13 | Chassis | Cisco Catalyst 9410R
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | OF Line Card | C9400-LC-12QC (12x40GE) | 12 | 280 | 954.8
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (IP Phone) | C9400-LC-48P | 48 | 845 | 250
|  | Line Card (AP) | C9400-LC-48UX | 48 | 1630 | 250 |  | Power required in chassis | 4380
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950 |  | Power provided by chassis | 9600
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Catalyst 9410R Fan Tray | C9410-FAN |  | 600 | 2046
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
Total | 39 |  |  |  |  | 14746.05
|  |  |  | Required UPS power [W] | 9600
|  |  |  | Available UPS power [W] | 20000
|  |  | Consum electric AC | Racire AC
| AC 1 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
| AC 2 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
|  | Total | 11400 | 38000
| Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 266
| Nr prize disponibil in PP UTP in acest rack | 336
Note on C31: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure
Note on C32: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure

## IDF2
Open Frame Server 44U Rack
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica W | Caldura disipata BTU/h | ORG Vert
Organizator de cabluri vertical | 1 | OF Patch Panel | PP-72X100G-SMF | 72 |  |  | Organizator de cabluri vertical
| 13 | Chassis | Cisco Catalyst 9410R
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | OF Line Card | C9400-LC-12QC (12x40GE) | 12 | 280 | 954.8
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (IP Phone) | C9400-LC-48P | 48 | 845 | 250
|  | Line Card (AP) | C9400-LC-48UX | 48 | 1630 | 250 |  | Power required in chassis | 4380
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950 |  | Power provided by chassis | 9600
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Catalyst 9410R Fan Tray | C9410-FAN |  | 600 | 2046
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
Total | 39 |  |  |  |  | 14746.05
|  |  |  | Required UPS power [W] | 9600
|  |  |  | Available UPS power [W] | 20000
|  |  | Consum electric AC | Racire AC
| AC 1 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
| AC 2 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
|  | Total | 11400 | 38000
| Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 280
| Nr prize disponibil in PP UTP in acest rack | 336
Note on C31: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure
Note on C32: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure

## IDF3
Open Frame Server 44U Rack
ORG Vert | Spatiu ocupat in U | Denumire/ tip echipament | Model | Scurta descriere/ nr porturi | Putere electrica W | Caldura disipata BTU/h | ORG Vert
Organizator de cabluri vertical | 1 | OF Patch Panel | PP-72X100G-SMF | 72 |  |  | Organizator de cabluri vertical
| 13 | Chassis | Cisco Catalyst 9410R
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | Supervisor | C9400-SUP-1XL | 2 | 350 | 1193.5
|  | OF Line Card | C9400-LC-12QC (12x40GE) | 12 | 280 | 954.8
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (WS) | C9400-LC-48P | 48 | 65 | 221.65
|  | Line Card (IP Phone) | C9400-LC-48P | 48 | 845 | 250
|  | Line Card (AP) | C9400-LC-48UX | 48 | 1630 | 250 |  | Power required in chassis | 4380
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950 |  | Power provided by chassis | 9600
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply | PWR-C4-3200WAC |  | 3200 | 950
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Power Supply |  |  |  | 0
|  | Catalyst 9410R Fan Tray | C9410-FAN |  | 600 | 2046
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 2 | UTP Patch Panel | CPPKL6ATG48WBL | 48
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
| 6 | UPS | SRT10KXLT |  | 10000 | 2450
Total | 39 |  |  |  |  | 14746.05
|  |  |  | Required UPS power [W] | 9600
|  |  |  | Available UPS power [W] | 20000
|  |  | Consum electric AC | Racire AC
| AC 1 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
| AC 2 | Daikin Sky Air Active Ducted Air Conditioner ADEAS60A | 5700 | 19000
|  | Total | 11400 | 38000
| Nr prize simple de conectat la acest DF, valoarea se ia din etapa 2 | 244
| Nr prize disponibil in PP UTP in acest rack | 336
Note on C31: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure
Note on C32: l7aur: +2 x APC SRT192BP2 => 20 minutes running time on failure